Abstract

AI data centers are entering resource adequacy planning as inflexible firm load, a treatment that reflects operational convention rather than physical necessity and that is increasingly difficult to sustain at the scale of projected demand. We show that inference-dominant facilities possess meaningful demand-side flexibility through spatial compute migration that current models do not capture. We develop a ten-parameter multiplicative cascade for spatial migration feasibility and test it against four years of day-ahead electricity pricing data across five U.S. grid regions, finding that at least one cross-region destination is unstressed during 99% or more of observed stress hours from each of four source zones tested. A conditional Monte Carlo simulation conditioned on observed per-hour grid states yields commitment depths that decline from 52% for an individual 500 MW facility to 25% for a 10 GW fleet, as co-stressed operators compete for finite destination capacity. The result has distinct implications for individual operators, who can credibly commit substantial flexibility above existing demand response baselines, and for system planners, who should not assume fleet-level contributions equal single-facility estimates.

1. Introduction

Rapid expansion of data center infrastructure is creating acute resource adequacy challenges in major U.S. electricity markets. In PJM Interconnection, data centers are projected to account for approximately 94% of 32 GW of peak demand growth through 2030 (ref. 1), contributing to a capacity position that deteriorates from a surplus of just 1,059 MW in the 2027/2028 delivery year to a projected deficit of 27 GW by 2035/2036 (ref. 2). Supply-side responses cannot keep pace: generation and storage projects face median completion timelines exceeding five years, with only 13% reaching commercial operation (ref. 3), and the underlying bottlenecks in permitting and equipment supply chains cannot be compressed by capital investment alone. Policy research has begun to argue that load flexibility should be the primary response. Norris and colleagues at Duke's Nicholas Institute demonstrated that data center loads willing to curtail during approximately 0.1% of annual hours could unlock roughly 100 GW of capacity using existing transmission infrastructure, translating to economic value exceeding $160/MW-day in constrained markets (ref. XX).

Resource adequacy planning has responded to this growth by treating data center load as firm and inelastic at each facility, requiring corresponding procurement of generating capacity plus reserve margin for every additional megawatt and allocating those costs to retail customers through capacity charges (ref. 4). This treatment reflects how data center operators have historically operationalized their service-level commitments to customers: contracts that guarantee uninterrupted compute have been satisfied by maintaining locally firm power draw at every facility, and planning models have inherited that local firmness as if it were a property of the load itself. The aggregation of these local firmness commitments across a rapidly growing fleet is what produces the system-level capacity requirement now exceeding what the interconnection queue can deliver. The gap between contracted compute and locally firm power is not a physical constraint, however. It is an operational convention, and one that an emerging line of research suggests is increasingly costly to maintain.

Recent work has begun to challenge one technical premise of this convention. In a field demonstration on a 256-GPU cluster, Colangelo et al. showed that software-based power management can reduce cluster power consumption by approximately 25% during peak demand periods through dynamic voltage-frequency scaling (DVFS) while maintaining service quality, and identified geographic workload migration as a promising spatial complement that remained unquantified (ref. 5). The geographic mechanism itself has prior foundations: Zheng, Chien, and Suh showed that shifting data center load from fossil-heavy to renewable-rich regions can mitigate curtailment and reduce emissions (ref. XX), and Zhang et al. developed a market-clearing framework in which spatially flexible data center loads participate as ‘virtual links’ in electricity markets (ref. XX). These contributions establish that compute is geographically movable and that market mechanisms can in principle accommodate that movement. What remains unquantified is whether spatial migration can provide committed, accreditable resource adequacy value during grid stress events, and under what conditions.

Here we quantify whether spatial compute migration can provide committed, accreditable resource adequacy value during grid stress events, and identify the conditions under which it does. We make three contributions. First, we introduce a ten-parameter multiplicative cascade that decomposes the conditions required for cross-region workload migration into independently estimable parameters, grading each against the best available empirical evidence. Second, we present a stress decorrelation analysis using four years of day-ahead locational marginal pricing data across five U.S. grid regions, establishing that at least one unstressed migration destination is available during 99% or more of observed stress hours from all source zones tested. Third, we develop a conditional Monte Carlo simulation that relaxed the cascade’s independence assumption, revealing that commitment depth is strongly scale-dependent, with the framework's conservatism diminishing as fleet size increases and destination contention becomes binding, a finding with direct implications for both capacity planning and infrastructure investment.

2. Decomposing spatial migration feasibility

We decompose spatial migration feasibility into ten multiplicative parameters spanning source-side candidacy, destination-side capacity, and execution reliability conditions. Source-side parameters capture whether workloads are geographically movable and operationally available for migration. Destination-side parameters capture whether cross-region destinations have the capacity and capability to receive migrating workloads. Execution parameters capture whether the migration can complete within grid dispatch windows. The effective spatial fraction is the product of all ten parameters, combined with DVFS applied to the non-migrating portion following Colangelo et al. (ref. 5). The framework's primary function is decomposition rather than point estimation: it identifies the conditions that must hold for spatial migration to succeed and grades each against available empirical evidence (see Methods for parameter definitions and empirical grounding).

3. Cross-region stress decorrelation

Spatial compute migration requires that at least one destination grid region is operating under normal conditions when the source region is stressed. We test this condition empicially using 35,060 hours of day-ahead locational marginal pricing (DA LMP) data from January 2022 through December 2025, spanning five U.S. grid regions: PJM, ERCOT, CAISO, MISO, and NYISO. Within each region we identify destination pricing zones co-located with verified data center facilities using the Baxtel database and U.S. Department of Energy county-level data center inventory (ref. 11, 12). Stress hours are defined as hours in which the DA LMP exceeds the 99th percentile of the zone’s own four-year distribution, yielding the 200 highest-priced hours per zone (see Methods for threshold sensitivity).

Using the ComEd zone in Northern Illinois as the primary source region, we compute the fraction of source stress hours in which at least one cross-region destination zone exhibits a DA LMP below its stress threshold. Of the 200 observed ComEd stress hours, at least one cross-region destination was available in 198, corresponding to a dynamic availability of 99.0%. The two failure hours occurred during the January 2024 Arctic Blast. The decorrelation structure reflects the electrical topology of the North American transmission system. ERCOT operates as an electrically isolated interconnection with no synchronous ties to the Eastern grid. CAISO has temporal offset and weather patterns that are largely independent from the Midwest. Capacity-weighted stress overlap between ComEd and cross-interconnection destinations ranges from 3.7% (ERCOT, summer) to 14.0% (CAISO, annual), with CAISO exhibiting zero summer overlap across the four-year study period (Fig. 3). Same-interconnection destinations exhibit substantially higher overlap: MISO zones range from 43% to 63%, and NYISO zones from 29% to 41%, consistent with shared exposure to regional weather systems and partial electrical coupling.

We replicate the analysis from three additional source zones to test generalization beyond the ComEd perspective: PJM-DOM (Northern Virginia, approximately 9,400 MW of installed data center capacity), ERCOT-LZ-NORTH (Dallas-Fort Worth), and CAISO-NP15 (Silicon Valley). Dynamic availability is 99.5% from PJM-DOM (one failure hour, the same 2024 Arctic Blast event) and 100% from both ERCOT-LZ-NORTH and CAISO-NP15 (Extended Data Table 1).

[FIGURE: Stress overlap heatmap showing capacity-weighted overlap between ComEd and each destination region]

4. Workload characterization

The operational timing parameter (S3) captures whether active inference requests at a source facility can complete within the grid operator’s emergency dispatch window. We validate drain time using two independent production inference datasets totaling 49.4 million requests over a combined 128 days of observation (see Mthods for dataset descriptions). P99 drain times range from 4.5 to 12.12 seconds across model configurations and datasets, approximately two orders of magnitude below PJM’s minimum dispatch window of 10 minutes (ref. 14), indicating that S3 = 0.90 is a conservative parameterization. The 10% excluded by S3 accomodates long-running or batched inference requests, multi-turn conversational session with persistent state, and potential future workload types with longer completion times (Fig. 4).

[FIGURE: Drain time cumulative distribution function, DynamoLLM vs. BurstGPT]

5. Conditional Monte Carlo validation

We develop a conditional Monte Carlo simulation that conditions on observed per-hour grid states to capture how commitment depth depends on fleet size and destination contention during specific stress events.

For a representative 500 MW inference-dominant facility, the conditional Monte Carlo yields a mean commitment depth of 52.0%, approximately 31 percentage points above the cascade estimate of 21.0% (Fig. 4a). The distribution exhibits a sharp upper concentration near 55.0% with a left tail extending to the DVFS floor of 17.5%. The 5th percentile (Value at Risk) is [CHRIS: v18 single-fac P5]%, and the conditional expected shortfall below the 5th percentile (CVaR) is 31.7%, indicating that even in the worst 5% of outcomes, commitment depth remains substantially above the DVFS-only baseline. The cascade's conservatism at single-facility scale arises from a ratio effect: the aggregate available headroom across unstressed destinations substantially exceeds the demand from a single migrating facility in the large majority of stress hours. Hardware compatibility and utilization constraints bind only when combined with low destination availability, which occurs in 2 of 200 observed stress hours. The independence assumption's error is, in this regime, favorable: the correlation between low D1 and low D2 reduces commitment depth in precisely the hours where aggregate headroom would have been sufficient regardless.

When the analysis is extended to simultaneous migration by geographically distributed facilities, commitment depth becomes scale-dependent. We first evaluate an empirical fleet defined by the geographic distribution of PJM data center capacity across load zones, with per-hour co-stress identified from the intra-PJM coincidence matrix described in Section 3. Only zones experiencing simultaneous stress contribute migrating load in each hour. The effective migrating fleet averages approximately [CHRIS: verify v18 mean migrating MW] across stress hours, with substantial variation driven by whether the Dominion zone in Northern Virginia (9,341 MW of data center capacity) is co-stressed with ComEd, which occurs in 36% of stress hours. This empirical fleet yields a mean commitment depth of 26.5% (Fig. 4b). The fleet CVaR at the 5th percentile is 18.0%, barely above the DVFS floor of 17.5%, indicating that spatial migration contributes negligible additional flexibility in the worst tail scenarios.

We then evaluate commitment depth as a continuous function of fleet size using a parametric sweep from 0.5 to 20 GW. Commitment depth declines steadily as destination contention becomes binding: 48.7% at 1 GW, 39.0% at 3 GW, 31.5% at 5 GW, 24.6% at 10 GW, and 22.2% at 15 GW. At 10 GW, [X]% of Monte Carlo combinations are destination-constrained, and the gap between the conditional Monte Carlo (24.6%) and the cascade estimate (21.0%) narrows to just 3.6 percentage points as destination contention absorbs the additional headroom that conditioning on observed states reveals. The 5th percentile converges toward the DVFS floor of 17.5% at fleet scales above 10 GW, indicating that spatial migration's incremental contribution diminishes as aggregate demand approaches destination pool capacity.

This scale dependence has distinct implications for different stakeholders. Individual data center operators can credibly commit flexibility well above the cascade estimate, with meaningful spatial contribution persisting even in the 5th percentile of outcomes. Grid planners and regulators should not assume fleet-level commitment depths equal single-facility estimates without accounting for destination capacity constraints. The transition from facility-scale to fleet-scale behavior occurs at approximately [X] GW, where destination contention becomes the binding constraint in the majority of stress hours.

6. System-level implications

The commitment depths estimated by the conditional Monte Carlo translate directly to resource adequacy contributions within existing capacity market frameworks. We evaluate system-level implications at two reference scales. For an individual 1 GW inference-dominant facility, the conditional Monte Carlo yields a mean commitment depth of 48.7%, implying approximately 487 MW of curtailable load during system emergencies, or approximately 448 MW when derated toa 92% effective load carrying capability (ELCC) consistent with PJM’s treatment of demand response resources (ref. 29). For an aggregate 10 GW fleet, destination contention reduces mean commitment depth to 24.6%, implying approximately 2,460 MW curtailable and 2,263 MW accredited. The per-MW economics are approximately scale-independent under the cascade model, but the absolute resource contribution exhibits diminishing returns above the contention onset of approximately [CHRIS: v18 contention onset] GW.

Two properties distinguish spatial migration from other grid flexibility resources. First, spatial migration can be activated at software timescales using existing multi-region compute infrastructure, though institutional mechanisms for grid commitment do not yet exist. Second, unlike electrochemical storage, which is duration-limited, spatial shifting sustains load reduction indefinitely because workloads are served remotely rather than deferred (ref. 5).

To estimate the economic value to the grid, we calculate avoided capacity costs using the capacity requirements identified in Energy + Environmental Economics' 2025 Resource Adequacy Study for Illinois and cost estimates from NREL's Annual Technology Baseline (ref. 32). At NREL's levelized combined-cycle cost of $180,000/MW-yr, the annualized avoided capacity cost is approximately $81 million for an individual 1 GW facility and approximately $407 million for a 10 GW fleet at the fleet commitment level. These figures represent the system planner's perspective: capacity procurement that spatial migration commitments would displace.

From the operator’s perspective, a distinct and substantially larger incentive may exist through interconnection acceleration. If a flexible interconnection framework allows a facility to energize before network upgrades complete, the present value of avoided delay depends on foregone compute revenue during the waiting period. An illustrative calculation using prevailing hyperscaler capital expenditure rates yields an interconnection acceleration value on the order of billions of dollars for a 1 GW facility over a three-year acceleration window (see Extended Data for assumptions and sensitivity). This estimate is highly sensitive to assumed revenue per MW and acceleration duration, but even under conservative assumptions the interconnection incentive exceeds direct capacity market revenue by at least an order of magnitude, suggesting that operators’ primary economic motivation under this framework derives from accelerated energization rather than capacity payments.

7. Discussion

Several limitations qualify these results. Most importantly, the three parameters that dominate model uncertainty: destination-side utilization headroom (D2, 44% of variance), inference workload share (D4, 28%), and pre-staging readiness (D5, 13%), are not directly observable in public data. For that reason, we do not interpret the model as providing precise universal estimate of accreditable flexibility for AI data centers. The contribution of the cascade and conditional Monte Carlo is to show that, after the physical feasibility of cross-region migration and the operational feasibility of dispatch window compliance are established empirically (Sections 3 and 4), the remaining uncertainty is concentrated in a small set of destination-side operational choices. The framework therefore identifies where operator behavior, disclosure, or contractual commitments would have the highest impact on realized resource adequacy value, and bounds the consequences of those choices across a plausible parameter space.

The nature of this concentrated uncertainty is decision-relevant rather than irreducible. D2 reflects how much GPU headroom operators choose to maintain at destination facilities. D4 tracks the allocation of compute between inference and training, a ratio shifting rapidly toward inference (refs. 11, 12). D5 captures whether operators invest in systematic model weight pre-staging across geographically diverse facilities. Each is an investment or operational decision, not a physical constraint. The gap between the physical potential for spatial migration and the realized commitment depth is therefore governed by institutional choices rather than physical constraints, and the variance decomposition identifies precisely which choices matter most.

Day ahead locational marginal pricing serves as a proxy for grid stress throughout this analysis. This choice is methodologically conservative: real-time price spikes are driven by local contingencies (generator forces outages, transmission deratings) that are less correlated across interconnection boundaries than the weather-drive supply-demand imbalances captured by day-ahead prices (ref. 33). The 92% ELCC applied in the system-level calculations follows PJM precedent for demand response resources (ref. 29), but the conditional Monte Carlo’s tail risk profile, particularly the fleet CvaR of 18.0% at the 5th percentile, suggests that a rigorous ELCC determination through sequential Monte Carlo reliability modeling may yield a different value.

The workload validation spans two production datasets totaling 49.4 million requests over a combined 128 days of observation. While both datasets represent genuine production inference traffic from major cloud providers, they reflect a limited window of operational conditions and a single provider ecosystem. The extent to which drain time distributions and temporal patterns generalize to other providers, model architectures, and deployment configurations remains an open empirical question, though the consistency of drain time results across two datasets provides partial cross-validation.

The fleet-level analysis reveals a finding with implications for both grid planning and infrastructure investment. Commitment depth is strongly scale-dependent, declining from 52.0% for individual facilities to 24.6% for a 10 GW fleet as simultaneous migration by co-stressed facilities saturates finite destination capacity. At individual facility scale, the cascade’s independence assumption introduces substantial conservative bias, and operators can credibly commit flexibility well above the cascade estimate. At fleet scale, the gap between the conditional Monte Carlo and the cascade narrows to 3.6 percentage points, and the two estimates converge at the 5th percentile. This divergence implies that accreditation frameworks should distinguish between individual facility commitments and fleet0level resource contributions, potentially through coordination requirements or portfolio-level verification protocols.

The coordination challenge identified at fleet scale points toward institutional mechanisms that do not yet exist in current electricity market designs. Aggregation of spatial migration commitments across multiple operators, analogous to demand response aggregation in existing capacity markets, could allocate destination headroom more efficiently than uncoordinated facility level decisions. Zhang et al.'s virtual link framework provides a formal basis for incorporating spatially flexible loads into market clearing (ref. XX), though its application to reliability-committed resources under the destination contention conditions identified here remains unexplored. The development of such mechanisms represents a precondition for fleet level spatial migration to achieve commitment depths substantially above the DVFS baseline in tail scenarios. We note that the analytical framework developed here, particularly the conditional Monte Carlo with operator-specific parameterization, provides a tool for quantifying the value such coordination would unlock, a question we develop in forthcoming work.

Each of the dominant destination-side parameters corresponds to a concrete policy or investment lever. The sensitivity surface (Fig. X) quantifies how fleet commitment depth varies across the plausible ranges of D2 and D5, the two parameters that span the widest uncertainty: mean commitment depth ranges from 20.7% to 30.3% at 10GW. The tornado chart confirms that D2, D4, and D5 together account for the full sensitivity range, while source-side parameters (S2, S3, D1) show near-zero sensitivity at fleet scale because the fleet is entirely destination-constrained. This result has a direct institutional implication: policies targeting source-side constraints (data locality waivers, regulatory flexibility) would increase individual facility commitment depth but have negligible effect at fleet scale, where destination-side investment is the binding constraint. Pre-staging readiness (D5) is the most directly actionable of the three: it requires no change in hardware or workload composition, only operational investment in model weight distribution across geographically diverse facilities.

Two regulatory mechanisms, designed to operate sequentially, could capture the flexibility quantified here within existing market structures. Under a flexible interconnection framework, a data center would energize before network upgrades complete, with a binding curtailment commitment that enters the grid operator’s planning models as reduced firm load. The required upgrades proceed in parallel, but the facility is not delayed by their completion. ERCOT’s connect-and-manage framework for generation resources provides a partial precedent (ref. 34). As grid positions mature, facilities may convert to full firm service and offer flexibility as formal demand response in capacity auctions, subject to the constraint that the same megawatt cannot simultaneously reduce the load forecast and be offered as demand response supply (ref. 35). The interconnection acceleration mechanism dominates the economic incentive for operators in the near term.

The central structural feature of this framework is a reallocation of reliability risk. Under current practice, the grid operator bears the full obligation to procure sufficient capacity to serve data center load at its nameplate rating, and procurement costs are allocated to retail customers. Under the framework proposed here, the data center operator assumes responsibility for managing a portion of its own power availability during system emergencies. The natural decorrelation of grid stress across interconnection boundaries, demonstrated empirically in Section 3, is a physical property of the North American transmission system. Exploiting it for resource adequacy purposes requires multi-region infrastructure that major data center operators have already constructed for commercial reasons (ref. 31), but activating it as a committed grid resource requires institutional mechanisms for verification, commitment, and compensation that remain to be developed.

Looking forward, the most valuable empirical contributions would be direct measurement of the three parameters that dominate framework uncertainty: GPU-level utilization distributions at candidate destination inference facilities (D2); the fraction of destination workloads running compatible inference (D4); and the operational readiness of model weight pre-staging at geographically diverse facilities (D5). The fleet coordination problem identified by the conditional Monte Carlo motivates development of allocation mechanisms, verification protocols, and potentially a specialized intermediary function analogous to existing demand response aggregators. These represent institutional infrastructure for spatial compute migration to contribute to resource adequacy at the scale the underlying physics would support.

Methods

Cascade parameter specifications. Table M1 reports the central value, distribution, and empirical basis for each of the ten cascade parameters. Source-side parameters: S1 (workload candidacy) = 0.70, representing the inference-dominant share of facility compute load; S2 (data locality) = 0.70, Uniform[0.60, 0.95], bounded by regulatory analysis of data residency requirements; S3 (operational timing) = 0.90, validated empirically in Section 4. Destination-side parameters: D1 (cross-region availability) is observed per-hour from pricing data rather than drawn parametrically; D2 (utilization headroom) = 0.33, Uniform[0.20, 0.50], anchored on measured GPU utilization rates of 50-80% at hyperscaler AI inference facilities (refs. 26, 27), representing GPU compute absorption capacity rather than facility-level load factor (the latter includes cooling, networking, and storage overhead that cannot absorb migrated inference workloads); D3 (hardware compatibility) = 0.88, held fixed based on CUDA/TensorRT backward compatibility rates in published market data; D4 (inference workload share) = 0.50, Uniform[0.33, 0.67], bounded by industry projections of inference as a share of total data center compute (refs. 11, 12); D5 (pre-staging readiness) = 0.65, Uniform[0.50, 0.80], representing the weakest empirical layer in the decomposition, estimated from operational practice at hyperscaler-operated facilities. Execution parameters: E1 (routing completion) = 0.95; E2 (bandwidth adequacy) = 0.98. The commitment depth formula Commitment Depth = Spatial + DVFS × (S1 - Spatial) applies DVFS only to the compute-amenable portion of facility load, following Colangelo et al.'s measurement at the GPU cluster level via nvidia-smi (ref. 5).

Variance decomposition. The cascade Monte Carlo (N = 50,000) draws all ten parameters independently from their specified distributions, computes the multiplicative product, and applies the commitment depth formula. First-order Sobol-style variance attribution is computed by fixing each parameter at its central value and measuring the reduction in output variance. This yields the variance shares reported in Section 2 (D2: 44%, D4: 28%, D5: 13%, S2: 13%). These shares are properties of the model's distributional assumptions, not of reality; their primary function is to identify which parameters most repay empirical measurement.

Stress threshold definition. Stress hours are defined as hours in which the day-ahead LMP exceeds the 99th percentile of the zone's own four-year distribution, yielding the 200 highest-priced hours per zone over the January 2022 through December 2025 observation period. Sensitivity analysis using alternative thresholds (98th and 99.5th percentiles) indicates that the cross-region decorrelation result is robust to threshold specification (Extended Data Fig. 1).

Workload datasets. The Microsoft Azure LLM Inference Dataset 2024 (DynamoLLM) comprises 44.1 million requests sampled from Azure production infrastructure over seven days in May 2024 (ref. 15). The BurstGPT dataset comprises 5.3 million requests from Azure OpenAI regional endpoints spanning 121 days of continuous observation (ref. 16). Both datasets represent production inference traffic. Drain times are computed at an assumed generation rate of 60 tokens per second; sensitivity to this assumption is reported in Extended Data Fig. 2. Diurnal usage patterns in DynamoLLM range from approximately 3× peak-to-trough for conversational workloads to 35× for coding workloads (ref. 15), while BurstGPT exhibits near-continuous 24-hour activity with minimal weekly periodicity, consistent with differing user populations (Azure OpenAI regional API traffic vs. Azure internal production workloads). These temporal divergences do not affect the S3 parameterization, which depends on per-request drain time rather than aggregate traffic volume.

Conditional Monte Carlo simulation. For each of the 200 ComEd stress hours, the simulation observes which destination zones are simultaneously stressed using DA LMP flags, replacing parametric D1 with binary per-hour, per-destination realizations. For each unstressed destination, D2, D4, and D5 are drawn independently from their specified uniform distributions; D3 is held fixed at 0.88. Available headroom at each destination is computed as destination capacity × D2 × D3 × D4 × D5. The migrating demand from the source facility (or fleet) is then allocated across destinations in proportion to available headroom, up to each destination's computed capacity. Commitment depth is the sum of migrated load plus DVFS applied to the non-migrating portion, divided by total facility (or fleet) capacity. 2,000 independent draws per stress hour yield 400,000 total samples. Source-side parameters (S1 = 0.70, S2 = 0.70, S3 = 0.90, E1 = 0.95, E2 = 0.98) are held at central values as structural or strongly grounded parameters.

Destination pool. The destination pool comprises 19 hourly-price zones across four grid regions: ERCOT (four zones), CAISO (two zones), MISO (eight zones), and NYISO (five zones). MISO Illinois is included despite geographic proximity to the ComEd source zone because MISO and PJM are independently dispatched with different generation mixes. WECC non-ISO bilateral trading hubs (Mid-Columbia, Palo Verde) are excluded because their published price data is daily-resolution, insufficient for hourly stress event detection. These excluded hubs represent approximately 9,900 MW of current data center capacity, or roughly 52% additional capacity beyond the 19-zone pool. Their inclusion would increase destination headroom and shift fleet commitment depth upward; reported figures are therefore conservative with respect to the full destination pool.

Per-GW parametric sweep. The fleet-level analysis evaluates commitment depth as a continuous function of fleet size from 0.5 to 20 GW. At each fleet size, the migrating demand in each stress hour is fleet_MW × S1 × S2 × S3 (the source-side cascade product). This demand competes for the same per-hour destination headroom computed in the conditional MC. The sweep identifies the contention onset (the fleet size at which more than 50% of draw-hour combinations become destination-constrained) and produces the commitment depth curve reported in Section 5.3.

Sensitivity analysis. The two-dimensional sensitivity surface evaluates fleet commitment depth (10 GW) across a 10 × 10 grid of D2 and D5 values, with D3 and D4 held at central values. Each grid point computes deterministic hour-by-hour commitment depth using the conditional MC framework. The tornado chart evaluates one-at-a-time sensitivity across all ten parameters at 10 GW, sweeping each from its lower to upper bound while holding others at central values.

System-level calculations. The 92% ELCC applied to committed MW follows PJM precedent for demand response resources (ref. 29). Avoided capacity cost is computed using the E3 levelized CT cost of $180,000/MW-yr from the E3 2025 Resource Adequacy Study for Illinois (ref. 32). The interconnection acceleration calculation is reported in Extended Data with full assumptions and sensitivity.

Data and Code Availability

Day-ahead LMP data are publicly available from PJM, ERCOT, CAISO, MISO, and NYISO market portals. The Microsoft Azure LLM Inference Dataset 2024 is available at [repository]. The BurstGPT dataset is available at [repository]. Data center location data are from Baxtel (baxtel.com and the U.S. Department of Energy. Analysis code and processed datasets will be made available upon publication.

AI Disclosure

The author used AI tools (Anthropic Claude) to assist with structural organization of the manuscript, literature search, and computational code development. All analysis, interpretation, and text are the author's own.

Acknowledgments

The author thanks R. Rosner and the Bartlett Fellowship in Energy Policy at the Energy Policy Institute at Chicago.]

Selected References

[1] Colangelo, M. et al. Software-based power management for AI data centers. Nature Energy (December 2025).

[2] PJM Interconnection. 2025 Long-Term Load Forecast (2025).

[3] PJM Interconnection. 2027/2028 Base Residual Auction Report (2025).

[4] E3 (Energy + Environmental Economics). 2025 Resource Adequacy Study for Illinois (2025).

[5] LBNL. Queued Up: Characteristics of Power Plants Seeking Transmission Interconnection (2024).

[6] NREL. 2024 Annual Technology Baseline. atb.nrel.gov/electricity/2024.

[7] FERC. Order on Transmission Service for Co-Located Load. 193 FERC ¶ 61,217, Docket Nos. EL25-49-000 et al. (December 18, 2025).

[8] Patel, P. et al. Splitwise: Efficient generative LLM inference using phase splitting. ISCA (2024).

[9] Stojkovic, J. et al. DynamoLLM: Designing LLM inference clusters for performance and energy efficiency. arXiv:2408.00741 (2024).

[10] Wang, Y. et al. BurstGPT: A real-world workload dataset for large language models. arXiv (2024).

[11] Deloitte. Technology, Media and Telecommunications Predictions 2025 (November 2025).

[12] McKinsey & Company. Investing in the rising data center economy (January 2025).

[Full bibliography to be compiled for submission]